| Design Analysis Section / Page No. | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |
| 46 | 1 | E. Scott | The Counting House PC load of 155 W in the computer room is too low. An average job specific PC is at least 250W and probably closer to 450W. There will probably be 15-20 LCD monitors adding ~100W each also |  |
| 46 | 2 | E. Scott | The Counting House PC load of 200 W outside the computer room is too low. An average desk PC is at least 350W and probably closer to 450W. The LCD monitor is ~100W on top of the case load. |  |
| ~63 | 3 | E. Scott | Power distribution: There is not specific language stating that the counting house computers, tagger user electronics and the Hall D user equipment will have separate transformers from the pump motors after the substation for "clean power". |  |
| A3 | 4 | E. Scott | Still no rails in the Hall D floor |  |
| A3-A5 | 5 | E. Scott | Location of floor drains to handle user generated condensation? |  |
| A5 | 6 | E. Scott | The conduit shield is lower than would be nice. How close to the beam can we get it? At a minimum it should be higher than the top of the door. |  |
| A7 | 7 | E. Scott | Orientation of the racks in the Rack Room is wrong. They need to face the “wall of glass and we only need 12 not 20. |  |
| A7 | 8 | E. Scott | Why do we have two outside entrances on the east side of the building? Push the dumbwaiter south change the single doors in to double and you gain more office space by making the existing VEST into user space. |  |
| A6, A10 | 9 | E. Scott | Why does the tagger have a dumbwaiter? |  |

| Concept Dwg No | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |

| Cost Estimate Section / Page | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |