| Design Analysis Section / Page No. | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |
| 23 |  | Kross | Truck access required to gas shed |  |
| 23, 47 |  | Kross | Gas shed requires insulation, heat, and ventilation |  |
| 23 |  | Kross | Gas shed should have reasonable proximity to counting house |  |
| 23 |  | Kross | Gas shed roof should extend over an adjacent pad ~8’ that can be fenced to store on-line and off-line gas bottles- fence enclosed |  |
| 56-57 |  | Kross | Hurricane barrier for truck ramp? |  |
|  |  | Kross | Smooth floor on truck ramp? Textured floor in existing truck ramps created problems |  |
| 55 |  | Kross | Reverse osmosis water system for chiller make up water? Located where? How large? |  |

| Concept Dwg No | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |

| Cost Estimate Section / Page | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |