| Design Analysis Section / Page No. |  |  | Cmt # | Reviewer | JLAB Review Comment | A/E Response |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 23 | 1 |  | Kross | Truck access required to gas shed and close proximity to counting house (See comment # 45) |  |  |
|  | 23 | 2 |  | Kross | Gas shed roof should extend over an adjacent pad ~8’ that can be fenced to store on-line and off-line gas bottles- fence enclosed |  |  |
|  | 23, 47 | 3 |  | Kross | Gas shed requires insulation, heat, and ventilation |  |  |
|  | 44 | 4 |  | R. Jones | The quadrupole magnet and PS is missing in the table under Hall D. The quadrupole PS power is 2.5 KVA and consumes 0.1 GPM. |  |  |
|  | 46 | 5 |  | E. Scott | The Counting House PC load of 155 W in the computer room is too low. We suggest using an average power consumption of 450W. There will also be 15-20 LCD monitors adding ~100W each also |  |  |
|  | 46 | 6 |  | E. Scott | The Counting House PC load of 200 W outside the computer room is too low. We suggest the use of an average power load of 450W. The LCD monitor is ~100W on top of the base load. |  |  |
|  | 47 | 7 |  | R. Jones | The collimator PS feeds two magnets in the collimator hut. The total LCW load is 10 KVA and 7 GPM, the total CHW load is 1 KVA and 1 GPM. |  |  |
|  | 47 | 8 |  | E. Smith | The number of racks in the counting house rack space should be increased to 18. |  |  |
|  | 55 | 9 |  | Kross | Reverse osmosis water system for chiller make up water? Located where? How large? |  |  |
|  | 56-57 | 10 |  | Kross | Hurricane flood barriers (gates) for truck ramp? (see also A3) |  |  |
|  | ~63 | 11 |  | E. Scott | Power distribution: There is not specific language stating that the counting house computers, tagger user electronics and the Hall D user equipment will have separate transformers from the pump motors after the substation for "clean power". |  |  |

| Concept Dwg No |  | Cmt # | Reviewer | JLAB Review Comment | A/E Response |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | A2 | 12 | E. Smith | Sections B and F/A8 in A2 are inconsistent with actual drawings |  |  |
|  | A2 | 13 | J Kellie | In tagger area, ground to beamline should be 1.8 m and floor to ceiling should be 4.5 m. |  |  |
|  | A2 | 14 | R. Jones | 10” beam pipe (heavy line) appears to begin about 5m downstream of the beam exit from the tagger area. It should begin inside the tagger area, downstream of the permanent magnet (dwg. A2). |  |  |
|  | A3 | 15 | E .Wolin | Add hole in west wall for photon beam into dump |  |  |
|  | A3 | 16 | E. Scott | Still no rails in the Hall D floor |  |  |
|  | A3 | 17 | E. Wollin | show PSS doors in access labyrinth |  |  |
|  | A3 | 18 | E. Smith | B-1 “counting house/ Hall D” ghost comment? |  |  |
|  | A3 | 19 | E. Smith | Pipe between tagger building and collimator hut for signal cables missing? |  |  |
|  | A3 | 20 | R. Jones | One or two penetrations through the exterior wall of the Hall D experimental area are requested by survey crew to enable line-of-sight to alignment fixtures inside the Hall from exterior locations on the site. |  |  |
|  | A3-A5 | 21 | E. Scott | Location of floor drains to handle user generated condensation? |  |  |
|  | A5 | 22 | E. Scott | D-3.5 Move conduit shield up above top of door (close to beam height) |  |  |
|  | A5 | 23 | E. Smith | D-3.5 'sheild' misspelled |  |  |
|  | A5 | 24 | E. Smith | C-1 “cryo-plant – beyond” ghost comment? |  |  |
|  | A6 | 25 | E. Wolin | move skid to open area |  |  |
|  | A6 | 26 | E. Wolin | Check upstream edge of permanent magnet to downstream wall distance is 13 m. (does not seem to scale off of drawing) |  |  |
|  | A6 | 27 | E. Wolin | eliminate jogs in tagger bldg walls |  |  |
|  | A6 | 28 | E. Wolin | Review hurricane flood gates protection into tagger building (see also comment 5) |  |  |
|  | A6 | 29 | E. Smith | C-1.5 label goniometer |  |  |
|  | A6 | 30 | E. Smith | C-1.5 label quadrupole |  |  |
|  | A6 | 31 | E. Smith | Electron beam dump. Show electron dump shielding filling tunnel (NIC) Relocate center of dump proper to 5 upstream of end of tunnel |  |  |
|  | A6 | 32 | J Kellie | The distance from the radiator to the intersection of the photon beamline and the main electron beam exit line from the tagger is ~6.334 m. The angle between these two lines is 13.40 deg. |  |  |
|  | A6 | 33 | J Kellie | The location of the main electron beam exit line with respect to the shielding walls into the electron beam dump area must be calculated using the information in Cmt #32. The exit line appears to be ~mid-way between the back wall of the vacuum chamber and the focal plane, whereas it is ~2 cm from the back wall. |  |  |
|  | A6 | 34 | J Kellie | The goniometer vacuum chamber houses the radiator and room must be provided for the goniometer vacuum chamber whose diameter will be ~0.5m. |  |  |
|  | A6 | 35 | J Kellie. | For the tagger since distances along the beamline are measured from the radiator, this should be clearly indicated. The distance from the radiator to the entrance to the first dipole is ~3 m. |  |  |
|  | A6 | 36 | R. Jones | Cross-sectional area of electron beam dump tunnel should be minimized, consistent with access requirements, because that tunnel area upstream of the dump itself must be filled with shielding materials prior to tagged beam operation. |  |  |
|  | A6, A10 | 37 | E. Scott | Dumbwaiter in tagger access not needed. |  |  |
|  | A7 | 38 | E. Scott and E. Smith | Front of the racks in the rack room should face the console room. The console and rack area should be about 30'x28', with the rack area with a single line of racks in an "L" shape around the console area of 20'x18'. The number of racks needed is 18. |  |  |
|  | A7 | 39 | General | Consolidate space on east side of building. For example, why do we have two outside entrances on the east side of the building? Push the dumbwaiter south change the single doors in to double and you gain more office space by making the existing VEST into user space. |  |  |
|  | A7 | 40 | E. Smith | Move gas shed to lawn area east of counting room |  |  |
|  | A8 | 41 | E. Smith | Height in tagger building should be 4.5 m (not 4.27) |  |  |
|  | A11 | 42 | E. Smith | Top left of gas shed dimension 6’0’’ should be 2’0’’ (metric is correct) |  |  |
|  | A11 | 43 | E. Smith | Consider cost impact of expanding gas shed to a 20’x20’ prefab building. |  |  |
|  | C2 | 44 | E Wolin | Verify traffic circulation pattern allows large trucks to back down into Hall D and tagger buildings |  |  |
|  |  | 45 | Kross | Smooth floor on truck ramp? Textured floor in existing truck ramps created problems |  |  |

| Cost Estimate Section / Page | Cmt # | Reviewer | JLAB Review Comment | A/E Response |
| --- | --- | --- | --- | --- |